Wind Resistance Calculation Report for 6m Single-Arm Integrated Solar Street Light Pole Against Level 15 Typhoon

Ⅰ. Calculation Basis

- Load Code for the Design of Building Structures GB 50009-2012

- Standard for Design of Steel Structures GB 50017-2017

- Design Working Condition: Level 15 Super Typhoon, ultimate wind speed 50.9m/s

- Unified steel material for all components: Q235 carbon structural steel

Ⅱ. Complete Design Parameters (Finalized Parameters for Single-Arm Project)

1. Main Parameters of Street Light Pole

- Pole height: 6m tapered round pole

- Top diameter: 70mm, bottom diameter: 150mm

- Wall thickness: 3.0mm

- Steel performance: Q235 steel, yield strength 235MPa, allowable bending stress 215MPa

- Lamp arm form: Single-side single lamp arm, one 1.5m horizontal overhanging arm

2. Light Parameters (Single Light)

- Light dimension: 1.07m×0.438m×0.195m

- Windward area of Light: 0.4687㎡

- Self-weight of Light: 15kg, vertical gravity: 147N

- Flange Base Plate Parameters

- Flange specification: 280mm×280mm×12mm

- Material: Q235 steel plate, allowable bending stress 215MPa

4. Anchor Bolt and Cage Parameters

- Bolt configuration: 4 pieces of M22 anchor bolts

- Effective cross-sectional area of bolt: 303mm²

- Embedded length of bolt: 600mm (0.6m)

- Bolt spacing: 200mm×200mm

- Allowable tensile stress of bolt: 170MPa

- Foundation concrete grade: C25

5. Basic Wind Load Parameters for Level 15 Typhoon

- Typhoon wind speed: 50.9m/s

- Air density: 1.25kg/m³

- Basic wind pressure: 1620N/㎡

- Wind load shape coefficient: 0.8 for light pole, 1.3 for lamp arm + Light

Ⅲ. Calculation of Wind Load and Total Overturning Moment at Pole Base

1. Wind Load on Pole Shaft

- Average outer diameter of pole = (70+150)÷2 = 110mm = 0.11m

- Windward area of pole = 0.11×6 = 0.66㎡

- Horizontal wind load on pole = 1620×0.8×0.66 = 855.36N

- Force acting point: Midpoint of pole shaft, 3m above ground

- Overturning moment generated by pole shaft = 855.36×3 = 2566.08N·m

2. Total Wind Load on Single Lamp Arm + Single Light

- Overall horizontal wind load of single Light = 1620×1.3×0.4687 = 986.3N

- Force acting point: Top of light pole, 6m above ground

- Overturning moment generated by single Light = 986.3×6 = 5917.8N·m

3. Total Overturning Moment at Pole Base (Most Unfavorable Force Condition)

- Total overturning moment = Overturning moment of pole shaft + Overturning moment of single Light

- Total M = 2566.08 + 5917.8 = 8483.88N·m

Supplementary Note on Light Self-weight

The 15kg Light produces a vertical downward pressure of 147N. As a vertical load, it does not increase the horizontal overturning moment. Instead, it can slightly offset the tensile force of anchor bolts, which is beneficial to the anchorage stress of the bolt cage and has no impact on the overall wind resistance verification result.

Ⅳ. Part 1: Strength Verification of 6m Light Pole with 3.0mm Wall Thickness

1. Section Dimensions at Pole Bottom

- Bottom outer diameter: 150mm

- Bottom inner diameter = 150 - 2×3 = 144mm

- Bending section modulus of circular pipe section: 39960mm³

2. Calculation of Actual Bending Stress of Pole Shaft

- Total moment conversion: 8483.88N·m = 8483880N·mm

- Maximum bending stress of pole shaft = Total moment ÷ Section modulus = 8483880 ÷ 39960 = 212.3MPa

3. Result Judgment

Actual stress 212.3MPa ＜ Allowable stress of Q235 steel 215MPa ✅  Under Level 15 typhoon condition, the 3mm wall thickness light pole is qualified in bending strength, with no risk of bending, deformation or fracture.

Ⅴ. Part 2: Stress Verification of 280×280×12 Flange Base Plate

- Force span of flange: Bolt center spacing 200mm, plate thickness 12mm

- Section modulus of flange: 4800mm³

- Maximum bending stress of flange plate = 8483880 ÷ 4800 = 176.7MPa

Result Judgment

Actual stress 176.7MPa ＜ 215MPa

✅  The 12mm thick 280×280 flange plate is fully qualified in bending resistance, punching shear resistance and local bearing capacity, with no cracking or deformation risk.

Ⅵ. Part 3: Comprehensive Verification of 4 M22×600mm Anchor Bolts

Force Description: Under the action of overturning moment, 2 windward bolts are in tension while the leeward concrete bears compression. All tensile force is borne by the 2 windward bolts with a force arm of 0.10m.

1. Calculation of Bolt Tensile Force

- Total tensile force of bolts = Total overturning moment ÷ Force arm = 8483.88 ÷ 0.10 = 84838.8N

- Tensile force borne by single M22 bolt = 84838.8 ÷ 2 = 42419.4N

2. Tensile Strength Verification of Bolt Body

- Tensile stress of single bolt = Single bolt tensile force ÷ Effective cross-sectional area = 42419.4 ÷ 303 = 140.0MPa

Bolt Strength Judgment

Actual stress 140.0MPa ＜ Specified allowable tensile stress 170MPa

✅  The M22 bolt body is qualified in tensile strength with no risk of fracture or plastic deformation.

3. Pull-out Resistance Verification of 0.6m Embedded Bolt in C25 Concrete

- Bolt outer diameter: 22mm, embedded depth: 600mm

- Concrete bonding strength: 1.8N/mm²

- Total bonding contact area between bolt and concrete: 41448mm²

- Ultimate pull-out resistance of single bolt: 74606.4N

Anchorage Pull-out Resistance Judgment

Actual bolt tensile force 42419.4N ＜ Ultimate pull-out resistance 74606.4N ✅  The anchor bolt with 0.6m embedded depth has sufficient bonding and holding force in C25 concrete foundation and will not be pulled out under typhoon load.

Ⅶ. Overall Safety Factor Summary Table for Single-Arm Street Light

| Component Name | Actual Stress / Tensile Force | Code Allowable Value | Safety Factor | Verification Result |
| --- | --- | --- | --- | --- |
| 6m Light Pole (3.0mm) | 212.3MPa | 215MPa | 1.01 | Qualified |
| 280×280×12 Flange Plate | 176.7MPa | 215MPa | 1.22 | Qualified |
| M22 Anchor Bolt (Body) | 140.0MPa | 170MPa | 1.21 | Qualified |
| M22 Bolt (Concrete Anchorage) | 42419.4N | 74606.4N | 1.76 | Qualified |

Ⅷ. Comprehensive Conclusion

This project adopts a 6m tapered single-arm street light pole (top 70mm / bottom 150mm, wall thickness 3.0mm), equipped with 1.5m single-side lamp arm and integrated solar Light (1.07m×0.438m, self-weight 15kg), matched with 280×280×12 flange plate and 4 pieces of M22×600mm anchor bolts, to resist Level 15 super typhoon with wind speed of 50.9m/s:

- The 3.0mm wall thickness light pole is qualified in bending strength with satisfactory safety margin;

- The 280×280×12mm flange plate fully meets typhoon load requirements in bending performance;

- The M22 anchor bolts pass the body tensile test, and the 0.6m embedded concrete anchorage has sufficient pull-out resistance margin.

The complete structure consisting of light pole, flange plate and anchor cage fully satisfies the wind resistance design requirements for Level 15 typhoon, and is eligible for formal production, foundation embedding, on-site installation and project completion acceptance.